FOB and FOC Iron Sulphur Filter Start-up Instructions
Check out our youtube video playlist installation videos here https://www.youtube.com/playlist?list=PLmnBltD77jBVGmOAkE8sqD7_EcD5t-LA1
· This unit is plumbed just like a water softener except that the drain line needs to be hard plumbed directly to this unit, preferably using ½” pex piping and hard plumbed at the drain connection.  As this unit releases compressed air when regenerating be sure drain line is attached securely at both ends and along it’s length to keep it from coming loose.

· After installation is completed and before turning water back on, rotate the bypass handles to the bypass position (see bypass valve diagram page) turn water on and check for leaks.
· Fully open a cold water faucet that does not have an aerator or screen.

· Allow water to run until clear to rid pipes of debris, which may have occurred during installation.
· The FOB(C) is now ready for testing and setup.  Plug in and set clock to correct time.  

1.     Press and hold the REGEN button for five seconds until the drive motor starts.   

        Wait until the motor stops and the display reads “Backwash”.  The backwash time  
  
        will begin to count down.

2.     Open the inlet handle of the bypass valve slightly allowing water to fill the tank 
           
        slowly in order to expel air out of the drain line and remove fines from the media, 
 
        gradually increase flow over 5-10 minutes. CAUTION:  If water flows too rapidly,  
 
        there will be a loss of media out of the drain.

3.     When the water is flowing steadily to the drain without the presence of air and is not

        discoloured, press the REGEN button to advance the control to the brine position.  
 
        The brine time will begin to count down.

4.     Fully open the inlet bypass valve handle (bypass is now in the diagnostic position)


        There should be a slow flow to the drain.  Allow FOB(C) to complete this cycle 

         itself 


5.     Fully open the outlet bypass valve and allow water to flow to drain through a faucet 
             
        that has no screen until water is clear.
 
Call Gary if you have any questions at 705 527-5900  
