HY02B05 Thermostat Manual

[image: image1.png]



Technical Data                             

· Power Supply: AC200-240V, 50/60HZ

· Load Current: 3A(Water Heating); 12A/16A(Electric Heating)

· Accuracy: ±0.5ºC                  

· Set-point Temperature Range: 5ºC - 60ºC

· Limit Temperature Range: 5-99℃

· Consumption: <0.3W             

· Temperature Sensor: NTC

· Size: 86*86*17mm (H*W*D)  

Features                                                         

· Large LCD screen with blue backlight display and double temperature display mode

· Time display (minutes, hours, weeks)

· 6 period programmable controlling temperature setting

· Internal and external temperature sensor for choice

· Room temperature display precision is 0.5,inner precision is 0.1

· Setting temperature meet user’s demand of room temperature

· Memory function when power failure, protect your setting from power failure

· Room temperature automatically calibration function

Button description                                       

	NO.
	signal
	Description

	1
	[image: image2.png]



	on / off

	2
	M
	Mode key: switch over auto/manual time interval control and temporary manual, long press enter into time interval setting function

	3
	[image: image3.png]



	Time setting: hours, minutes, weeks setting.

	4
	[image: image4.png]



	Increase temperature, cooperate M and [image: image5.png]


 to setting

	5
	[image: image6.png]



	Decrease temperature, cooperate M and [image: image7.png]


 to setting


Function and display                                                             

“[image: image8.png]


”manual control(temporary manual control when flashing, auto control when no this sign display)
“[image: image9.png]


” it is heating;                         “[image: image10.png]


” open anti-freezing function;

“[image: image11.png]


” get up in morning, the first time interval;  “[image: image12.png]N



” go out in morning ,the second time interval;

“[image: image13.png]e



” back home at noon, the third time interval;“[image: image14.png]T



” go out at noon ,the fourth time interval;

“[image: image15.png]Ve



” back home at night, the fifth time interval; “[image: image16.png]


” sleep at night, the sixth time interval;

Operation                             
1) Setting hour ,min and week

Under power on state , press [image: image17.png]


,then press [image: image18.png]


 or [image: image19.png]


 to adjust . next press[image: image20.png]


 to pass next step   
2)Programmable

Under power on state ,long press M to program. then press [image: image21.png]


or[image: image22.png]


 to choose 5+2 days programmable ,6+1 days programmable or 7 days programmable 

Under power on state ,long press M to program. then press M to setting temperature, time. press[image: image23.png]


Or [image: image24.png]


 to adjust 

Time interval programming                                         
	Period
	Icon
	Default Period Time
	Default Period Temperature

	     Working Day
	1
	[image: image25.png]



	06:00
	20℃

	
	2
	[image: image26.png]N




	08:00
	15℃

	
	3
	[image: image27.png]e




	11:30
	15℃

	
	4
	[image: image28.png]T




	12:30
	15℃

	
	5
	[image: image29.png]Ve




	17:30
	22℃

	
	6
	[image: image30.png]



	22:00
	15℃

	       Weekend
	1
	[image: image31.png]



	08:00
	22℃

	
	2
	[image: image32.png]



	23:00
	15℃


Advanced Setting(suggestion: operated by technician)         

At the same time ,Press [image: image33.png]


and [image: image34.png]


 key to enter advanced setting       
	No.
	Symbols
	Setting Item
	Parameter Setting Function
	Factory Default

	1
	SEN
	Sensor control option
	0:internal sensor

1:external sensor

2:internal control temperature,

  external limit temperature
	0:internal sensor



	2
	OSV
	Limit temperature value

of external sensor
	5-99℃
	42℃

	3
	dIF
	Return difference of limit

temperature value of

external sensor
	1-9℃
	2℃

	4
	SVH
	Set upper limit

temperature value
	5-99℃
	35℃

	5
	SVL
	Set lower limit

temperature value
	5-99℃
	5℃

	6
	AdJ
	Measure temperature
	Measure temperature, check and 

calibration
	0.1℃ precision

Calibration (actual

 temperature)

	7
	FrE
	Anti-freezing function
	00:anti-freezing function shut down

01:anti-freezing function open
	00:anti-freezing function

shut down



	8
	POn
	Power on memory 
	00:Power on no need memory

01:Power on need memory
	00:Power on no need memory

	9
	FAC


	Factory default
	08:just display, no other meaning

00:Restore factory default
	08


Note: Hysteresis (return temperature) description: the factory default of external sensor limit temperature(OSV) set as 42℃, external sensor limit temperature hysteresis(dIF) set as 2,when temperature up to 44℃,relay stop output, when temperature drops to 40℃,relay output again and heating.(operation when room temperature lower than setting temperature)
Sensor fault hint                                                   
Please select internal, external sensor working mode correctly. If it is choose wrong or sensor is fault (breakdown),LCD interface will display “Err”, temperature controller stops heating until fault is eliminated. Special Hint: installation cable 

Please select: water heating selects 1.5-2.5mm2 rigid line; electric heating select above 2.5mm2 rigid line.
Power wiring diagram                                               

  [image: image35.png]N

AC230V  Imax18A

L1

LOAD

N1

1

2

IS



[image: image36.png]Close




[image: image37.jpg]



 Electric heating wiring diagram      Water heating wiring diagram             Water heating no contact wiring diagram

                                                                      (disconnection when electric valve close)                                                        
Installation                                                       
Warning: please wiring right strictly according to the wiring diagram, do not make water, mud and other debris into the thermostat, otherwise it will cause thermostat damage!

	[image: image38.jpg]



	[image: image39.jpg]



	[image: image40.jpg]



	[image: image41.jpg]




	1,open main control panel, with 3.5mm slotted point screwdriver along the inclined plane until to card depths of 4mm, pry up

slightly to open the card hook
	2,connect back panel and power, wire as per wiring diagram, fasten back panel on cassette with M4 screw
	3,connect winding

displacement of back panel and upper panel
	4,Hang up with 30° to 2 hooks, press on the 2 bottom corners, stuck on the upper shell, installation finished.



